## Instructions
3-phase Capacity Planning Tool - INSTRUCTIONS
USE ONLY FOR: 208V, 3phase INPUT; wired for 208V OUTPUT!
Welcome to the Raritan 3-phase capacity planning tool. These vendor-agnostic spreadsheets aim to demystify the process of correctly loading 3-phase rack power strips -- to ensure maximum power capacity while preventing overloading.
1 | Five power strip capacity options are found below (worksheet tabs). It is VERY IMPORTANT to choose the correct planning tool sized for your rack power strip. Consult the spec sheet or engineering submittals of your rack power strip, to determine its rated input current -- not just the input plug type.
2 | For each outlet type (C13 or C19), per breaker -- enter in expected loads (in watts); and optionally, the name of the device drawing the load. For Tier II (and above) redundancy situations, complete the spreadsheet assuming that the other (redundant) power strip in the cabinet is offline.
3 | The capacity planning tool will automatically highlight any error conditions. So long as the field "capacity check" in the bottom-righ of the spreadsheet reads "OK" (Green), your rack power strip has not exceeded its capacity constraints.
4 | Optionally, adjust the input voltage and power factor assumptions (defaulted to 208V and 97.5% power factors, which are common in North America).
BE CAREFUL to choose the correct power strip capacity worksheet:
60A plug | Note that rack power strip vendors provide multiple products with 60A plugs (IEC 60309 60A 3P4W), but with two different rated currents: either 48A or 45A. (This is because 45A units require smaller, 6# AWG cable -- while 48A units are equipped with 4# AWG cable). Be sure to select the correct worksheet that corresponds to your power strip.
50A plug | Note that rack power strip vendors provide products with 50A plugs (Hubbell CS8365C, "California Style"), but with two different rated currents: either 40A or 35A. (This is because 35A units are equipped with only 3 branch circuit breakers -- while 40A units are equipped with 6 branch circuit breakers). Be sure to select the correct worksheet that corresponds to your power strip.
© 2016 Raritan Inc. - by Michael Suchoff and Henry Hsu

## 20A (16A ¦ 5.8kVA)
© 2016 Raritan Inc. by Michael Suchoff and Henry Hsu;
3-phase Capacity Planning Worksheet: 208V, 3phase / 20A (16A) per line
L1/L2 [XY] | [6 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Input Voltage
208
typical = 208
| Type | Device Name |  |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps
| Circuit Breaker A (L1/L2) | [6 empty] | Circuit Breaker B (L2/L3) | [5 empty] | Circuit Breaker C (L3/L1) | [5 empty] | Power Factor
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 1of5 |  | 250 | 1.2327 |  | 97.5%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 2of5 |  | 250 | 1.2327 |  | typical = above 95%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 3of5 |  | 250 | 1.2327
| C13 | ExchangeServer WEST |  |  | 350 | 1.7258 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 4of5 |  | 250 | 1.2327
| C13 | ExchangeServer EAST |  |  | 350 | 1.7258 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 5of5 |  | 250 | 1.2327
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | Current by Line Pair
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L1/L2 | 10.6016
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L2/L3 | 7.1499
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L3/L1 | 6.1637
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | Phase Balance
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L1 | 105.7%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L2 | 111.3%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L3 | 83.03%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | maximize capacity by balancing load
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | Capacity Remaining
| C19 | Cisco Nexus 7000, PS1 |  |  | 1450 | 7.1499 |  | C19 | Cisco Nexus 7000, PS2 |  | 1450 | 7.1499 |  | C19 |  |  |  | 0 |  | L1 | 8.204%
| C13 cannot exceed 12A; C19 cannot exceed 16A | [6 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | L2 | 3.315%
|  | OK | [6 empty] | OK | [5 empty] | OK |  |  |  |  | L3 | 27.87%
| 14.6873 |  |  | 15.4696 |  |  | 11.5404 |  |  | 4.9744 | [5 empty] | OK
| L1 Current (A) |  |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check
| cannot exceed 16A |  |  | cannot exceed 16A |  |  | cannot exceed 16A |  |  | cannot exceed 5.8kVA | [8 empty] | version 8

## 30A (24A ¦ 8.6kVA)
© 2016 Raritan Inc. by Michael Suchoff and Henry Hsu;
3-phase Capacity Planning Worksheet: 208V, 3phase / 30A (24A) per line
L1/L2 [XY] | [6 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Input Voltage
208
typical = 208
| Type | Device Name |  |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps
| Circuit Breaker A (L1/L2) | [6 empty] | Circuit Breaker B (L2/L3) | [5 empty] | Circuit Breaker C (L3/L1) | [5 empty] | Power Factor
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 1of5 |  | 250 | 1.2327 |  | 97.5%
| C13 |  |  |  |  | 0 |  | C13 | RAID Array 1 |  | 275 | 1.356 |  | C13 | CorpWebSvr 2of5 |  | 250 | 1.2327 |  | typical = above 95%
| C13 |  |  |  |  | 0 |  | C13 | RAID Array 2 |  | 275 | 1.356 |  | C13 | CorpWebSvr 3of5 |  | 250 | 1.2327
| C13 | ExchangeServer WEST |  |  | 350 | 1.7258 |  | C13 | RAID Array 3 |  | 275 | 1.356 |  | C13 | CorpWebSvr 4of5 |  | 250 | 1.2327 |  | Current by Breaker
| C13 | ExchangeServer EAST |  |  | 350 | 1.7258 |  | C13 | RAID Array 4 |  | 275 | 1.356 |  | C13 | CorpWebSvr 5of5 |  | 250 | 1.2327 |  | A | 10.6016
| C13 |  |  |  |  | 0 |  | C13 | RAID Array 5 |  | 275 | 1.356 |  | C13 |  |  |  | 0 |  | B | 13.93
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C | 12.0809
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | no breaker to exceed 20A
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | OK
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | SAP AppServer A |  | 600 | 2.9586
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | SAP AppServer B |  | 600 | 2.9586 |  | Current by Line Pair
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L1/L2 | 10.6016
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L2/L3 | 13.93
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L3/L1 | 12.0809
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | Phase Balance
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | L1 | 92.85%
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | L2 | 100.7%
| C19 | Cisco Nexus 7000, PS1 |  |  | 1450 | 7.1499 |  | C19 | Cisco Nexus 7000, PS2 |  | 1450 | 7.1499 |  | C19 |  |  |  | 0 |  | L3 | 106.5%
| C13 cannot exceed 12A; C19 cannot exceed 16A | [6 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | maximize capacity by balancing load
|  | OK | [6 empty] | OK | [5 empty] | OK
Capacity Remaining
| 19.6569 |  |  | 21.3099 |  |  | 22.5449 |  |  | 7.6154 | [5 empty] | OK |  |  |  | L1 | 18.1%
[20 empty] | L2 | 11.21%
| L1 Current (A) |  |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check |  |  |  | L3 | 6.063%
| cannot exceed 24A |  |  | cannot exceed 24A |  |  | cannot exceed 24A |  |  | cannot exceed 8.6kVA | [8 empty] | version 8

## 50A (35A ¦ 12.5kVA)
© 2016 Raritan Inc. by Michael Suchoff and Henry Hsu;
3-phase Capacity Planning Worksheet: 208V, 3phase / 50A (35A) per line
L1/L2 [XY] | [6 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Input Voltage
208
typical = 208
| Type | Device Name |  |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps
| Circuit Breaker A (L1/L2) | [6 empty] | Circuit Breaker B (L2/L3) | [5 empty] | Circuit Breaker C (L3/L1) | [5 empty] | Power Factor
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 1of5 |  | 250 | 1.2327 |  | 97.5%
| C13 |  |  |  |  | 0 |  | C13 | RAID Array 1 |  | 275 | 1.356 |  | C13 | CorpWebSvr 2of5 |  | 250 | 1.2327 |  | typical = above 95%
| C13 |  |  |  |  | 0 |  | C13 | RAID Array 2 |  | 275 | 1.356 |  | C13 | CorpWebSvr 3of5 |  | 250 | 1.2327
| C13 | ExchangeServer WEST |  |  | 350 | 1.7258 |  | C13 | RAID Array 3 |  | 275 | 1.356 |  | C13 | CorpWebSvr 4of5 |  | 250 | 1.2327 |  | Current by Breaker
| C13 | ExchangeServer EAST |  |  | 350 | 1.7258 |  | C13 | RAID Array 4 |  | 275 | 1.356 |  | C13 | CorpWebSvr 5of5 |  | 250 | 1.2327 |  | A | 10.6016
| C13 |  |  |  |  | 0 |  | C13 | RAID Array 5 |  | 275 | 1.356 |  | C13 |  |  |  | 0 |  | B | 13.93
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C | 15.0394
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | no breaker to exceed 20A
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | OK
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | SAP AppServer A |  | 600 | 2.9586
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | SAP AppServer B |  | 600 | 2.9586 |  | Current by Line Pair
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | SAP AppServer C |  | 600 | 2.9586 |  | L1/L2 | 10.6016
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L2/L3 | 13.93
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L3/L1 | 15.0394
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | Phase Balance
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | L1 | 97.42%
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | L2 | 93.03%
| C19 | Cisco Nexus 7000, PS1 |  |  | 1450 | 7.1499 |  | C19 | Cisco Nexus 7000, PS2 |  | 1450 | 7.1499 |  | C19 |  |  |  | 0 |  | L3 | 109.6%
| C13 cannot exceed 12A; C19 cannot exceed 16A | [6 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | maximize capacity by balancing load
|  | OK | [6 empty] | OK | [5 empty] | OK
Capacity Remaining
| 22.3157 |  |  | 21.3099 |  |  | 25.0942 |  |  | 8.2308 | [5 empty] | OK |  |  |  | L1 | 36.24%
[20 empty] | L2 | 39.11%
| L1 Current (A) |  |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check |  |  |  | L3 | 28.3%
| cannot exceed 35A |  |  | cannot exceed 35A |  |  | cannot exceed 35A |  |  | cannot exceed 12.5kVA | [8 empty] | version 8

## 50A (40A ¦ 14.4kVA)
© 2016 Raritan Inc. by Michael Suchoff and Henry Hsu;
3-phase Capacity Planning Worksheet: 208V, 3phase / 50A (40A) per line
L1/L2 [XY] | [6 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Input Voltage
208
typical = 208
| Type | Device Name |  |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps
| Circuit Breaker A (L1/L2) | [6 empty] | Circuit Breaker C (L2/L3) | [5 empty] | Circuit Breaker E (L3/L1) | [5 empty] | Power Factor
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 1of5 |  | 250 | 1.2327 |  | 97.5%
| C13 |  |  |  |  | 0 |  | C13 | 48-port OOB Switch |  | 275 | 1.356 |  | C13 | CorpWebSvr 2of5 |  | 250 | 1.2327 |  | typical = above 95%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 3of5 |  | 250 | 1.2327
| C13 | ExchangeServer WEST |  |  | 350 | 1.7258 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | Current by Breaker |  | no breaker to exceed 20A
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | A | 11.0947
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | B | 8.8757
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C | 10.7249
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | D | 7.1499
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | E | 13.0671
| C19 | UCS Chassis PS1 |  |  | 1900 | 9.3688 |  | C19 | UCS Chassis PS2 |  | 1900 | 9.3688 |  | C19 | UCS Chassis PS3 |  | 1900 | 9.3688 |  | F | 2.4655
OK
| Circuit Breaker B (L1/L2) | [6 empty] | Circuit Breaker D (L2/L3) | [5 empty] | Circuit Breaker F (L3/L1)
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 4of5 |  | 250 | 1.2327 |  | Current by Line Pair
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 5of5 |  | 250 | 1.2327 |  | L1/L2 | 19.9704
| C13 | ExchangeServer EAST |  |  | 350 | 1.7258 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L2/L3 | 17.8748
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L3/L1 | 15.5325
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | Phase Balance
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L1 | 99.9%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L2 | 106.3%
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | L3 | 93.84%
| C19 | Cisco Nexus 7000, PS1 |  |  | 1450 | 7.1499 |  | C19 | Cisco Nexus 7000, PS2 |  | 1450 | 7.1499 |  | C19 |  |  |  | 0 |  | maximize capacity by balancing load
| C13 cannot exceed 12A; C19 cannot exceed 16A | [6 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A
|  | OK | [6 empty] | OK | [5 empty] | OK
Capacity Remaining
[20 empty] | L1 | 22.94%
| 30.8255 |  |  | 32.7914 |  |  | 28.9551 |  |  | 11.1026 | [5 empty] | OK |  |  |  | L2 | 18.02%
[20 empty] | L3 | 27.61%
| L1 Current (A) |  |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check
| cannot exceed 40A |  |  | cannot exceed 40A |  |  | cannot exceed 40A |  |  | cannot exceed 14.4kVA | [8 empty] | version 8

## 60A (45A ¦ 17.3kVA)
© 2016 Raritan Inc. by Michael Suchoff and Henry Hsu;
3-phase Capacity Planning Worksheet: 208V, 3phase / 60A (45A) per line
L1/L2 [XY] | [6 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Input Voltage
208
typical = 208
| Type | Device Name |  |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps
| Circuit Breaker A (L1/L2) | [6 empty] | Circuit Breaker C (L2/L3) | [5 empty] | Circuit Breaker E (L3/L1) | [5 empty] | Power Factor
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 1of5 |  | 250 | 1.2327 |  | 97.5%
| C13 |  |  |  |  | 0 |  | C13 | 48-port OOB Switch |  | 275 | 1.356 |  | C13 | CorpWebSvr 2of5 |  | 250 | 1.2327 |  | typical = above 95%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 3of5 |  | 250 | 1.2327
| C13 | ExchangeServer WEST |  |  | 350 | 1.7258 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | Current by Breaker |  | no breaker to exceed 20A
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | A | 11.0947
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | B | 8.8757
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C | 10.7249
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | D | 16.4694
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | E | 13.0671
| C19 | UCS Chassis PS1 |  |  | 1900 | 9.3688 |  | C19 | UCS Chassis PS2 |  | 1900 | 9.3688 |  | C19 | UCS Chassis PS3 |  | 1900 | 9.3688 |  | F | 2.4655
OK
| Circuit Breaker B (L1/L2) | [6 empty] | Circuit Breaker D (L2/L3) | [5 empty] | Circuit Breaker F (L3/L1)
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 4of5 |  | 250 | 1.2327 |  | Current by Line Pair
| C13 |  |  |  |  | 0 |  | C13 | SAP AppSvr 1of3 |  | 630 | 3.1065 |  | C13 | CorpWebSvr 5of5 |  | 250 | 1.2327 |  | L1/L2 | 19.9704
| C13 | ExchangeServer EAST |  |  | 350 | 1.7258 |  | C13 | SAP AppSvr 2of3 |  | 630 | 3.1065 |  | C13 |  |  |  | 0 |  | L2/L3 | 27.1943
| C13 |  |  |  |  | 0 |  | C13 | SAP AppSvr 3of3 |  | 630 | 3.1065 |  | C13 |  |  |  | 0 |  | L3/L1 | 15.5325
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | Phase Balance
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L1 | 84.62%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L2 | 112.6%
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | L3 | 102.8%
| C19 | Cisco Nexus 7000, PS1 |  |  | 1450 | 7.1499 |  | C19 | Cisco Nexus 7000, PS2 |  | 1450 | 7.1499 |  | C19 |  |  |  | 0 |  | maximize capacity by balancing load
| C13 cannot exceed 12A; C19 cannot exceed 16A | [6 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A
|  | OK | [6 empty] | OK | [5 empty] | OK
Capacity Remaining
[20 empty] | L1 | 31.5%
| 30.8255 |  |  | 41.005 |  |  | 37.459 |  |  | 13.041 | [5 empty] | OK |  |  |  | L2 | 8.878%
[20 empty] | L3 | 16.76%
| L1 Current (A) |  |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check
| cannot exceed 45A |  |  | cannot exceed 45A |  |  | cannot exceed 45A |  |  | cannot exceed 16.2kVA | [8 empty] | version 8

## 60A (48A ¦ 17.3kVA)
© 2016 Raritan Inc. by Michael Suchoff and Henry Hsu;
3-phase Capacity Planning Worksheet: 208V, 3phase / 60A (48A) per line
L1/L2 [XY] | [6 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Input Voltage
208
typical = 208
| Type | Device Name |  |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps |  | Type | Device Name |  | Watts | Amps
| Circuit Breaker A (L1/L2) | [6 empty] | Circuit Breaker C (L2/L3) | [5 empty] | Circuit Breaker E (L3/L1) | [5 empty] | Power Factor
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 1of5 |  | 250 | 1.2327 |  | 97.5%
| C13 |  |  |  |  | 0 |  | C13 | 48-port OOB Switch |  | 275 | 1.356 |  | C13 | CorpWebSvr 2of5 |  | 250 | 1.2327 |  | typical = above 95%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 3of5 |  | 250 | 1.2327
| C13 | ExchangeServer WEST |  |  | 350 | 1.7258 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | Current by Breaker |  | no breaker to exceed 20A
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | A | 11.0947
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | B | 8.8757
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C | 10.7249
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | D | 16.4694
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | E | 13.0671
| C19 | UCS Chassis PS1 |  |  | 1900 | 9.3688 |  | C19 | UCS Chassis PS2 |  | 1900 | 9.3688 |  | C19 | UCS Chassis PS3 |  | 1900 | 9.3688 |  | F | 2.4655
OK
| Circuit Breaker B (L1/L2) | [6 empty] | Circuit Breaker D (L2/L3) | [5 empty] | Circuit Breaker F (L3/L1)
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 | CorpWebSvr 4of5 |  | 250 | 1.2327 |  | Current by Line Pair
| C13 |  |  |  |  | 0 |  | C13 | SAP AppSvr 1of3 |  | 630 | 3.1065 |  | C13 | CorpWebSvr 5of5 |  | 250 | 1.2327 |  | L1/L2 | 19.9704
| C13 | ExchangeServer EAST |  |  | 350 | 1.7258 |  | C13 | SAP AppSvr 2of3 |  | 630 | 3.1065 |  | C13 |  |  |  | 0 |  | L2/L3 | 27.1943
| C13 |  |  |  |  | 0 |  | C13 | SAP AppSvr 3of3 |  | 630 | 3.1065 |  | C13 |  |  |  | 0 |  | L3/L1 | 15.5325
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | Phase Balance
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L1 | 84.62%
| C13 |  |  |  |  | 0 |  | C13 |  |  |  | 0 |  | C13 |  |  |  | 0 |  | L2 | 112.6%
| C19 |  |  |  |  | 0 |  | C19 |  |  |  | 0 |  | C19 |  |  |  | 0 |  | L3 | 102.8%
| C19 | Cisco Nexus 7000, PS1 |  |  | 1450 | 7.1499 |  | C19 | Cisco Nexus 7000, PS2 |  | 1450 | 7.1499 |  | C19 |  |  |  | 0 |  | maximize capacity by balancing load
| C13 cannot exceed 12A; C19 cannot exceed 16A | [6 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A
|  | OK | [6 empty] | OK | [5 empty] | OK
Capacity Remaining
[20 empty] | L1 | 35.78%
| 30.8255 |  |  | 41.005 |  |  | 37.459 |  |  | 13.041 | [5 empty] | OK |  |  |  | L2 | 14.57%
[20 empty] | L3 | 21.96%
| L1 Current (A) |  |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check
| cannot exceed 48A |  |  | cannot exceed 48A |  |  | cannot exceed 48A |  |  | cannot exceed 17.3kVA | [8 empty] | version 8